## CAISO
Project Name | SUB_1 | SUB_2 | Utility | Project Type | Voltage (kV) | Distance (mi) | Rating | Cost ($ M) | Status | Planned Year | Description
Julian Hinds - Mirage 230 kV Advanced Reconductor Project | JULIAN HINDS | MIRAGE | SCE | Reliability | 230 | 47 | 1525 /1625 A | 76 | Planned | 2030 | Contingency analysis indicates that the updated line ratings would effectively mitigate the thermal overloads without the need to activate the Blythe RAS. Serving as a vital corridor for solar and battery storage in Riverside County, this project will utilize ACCC® conductors to increase ampacity and reduce energy losses. These upgrade costs are expected to be partially subsidized by the U.S. Department of Energy GRIP grant funding awarded through the CHARGE 2T project.
Reconductor of GWF – Kingsburg 115 kV line | KINGSBURG | GWF 2 | PG&E | Policy | 115 | 22 | 1500 A | 81.6 | Planned | 2029 | Mitigate overloads identified in the on-peak baseline deliverability study and support SB 100 clean energy goals. Likely to utilize high-capacity advanced conductors, such as CTC Global's ACCC®, for increased efficiency. This would need to update the limiting components at the substations if there is any. Protection may also need to be upgraded.
Eagle Rock-Fulton-Silverado _1 115 kV Line Reconductor | EAGLE ROCK | FULTON | PG&E | Policy | 115 | 27 | 1236 A | 92.9 | Planned | 2031 | Reconductor Eagle Rock-020/087A and update any limiting components at the substation (may require relay upgrades). These upgrades will support the integration of renewable resources and contribute to California's ambitious SB 100 clean energy goals.
Eagle Rock-Fulton-Silverado _2 115 kV Line Reconductor | FULTON | SILVERADO | PG&E | Policy | 115 | 3 | 1687 A | 92.9 | Planned | 2031 | Reconductor 020/87A-037/191A and update any limiting components at the substation (if any). These upgrades will support the integration of renewable resources and contribute to California's ambitious SB 100 clean energy goals.
El Patio – San Jose A 115 kV Line Reconductor | SAN JOSE STA. A | EL PATIO | PG&E | Reliability | 115 | 0.01 | 3000 A | 217 - 434 | Planned | 2032 | The set of 115 kV reinforcements proposed in this project, along with the major 500 kV transmission new project for the Bay Area and the re-scoping of two other projects in the San Jose area, will provide sufficient transmission capacity to meet long-term load growth needs.
Trimble – San Jose B 115 kV Line Reconductor | SAN JOSE STA. B | TRIMBLE | PG&E | Reliability | 115 | 3.65 | 3000 A | 217 - 434 | Planned | 2032 | The set of 115 kV reinforcements proposed in this project, along with the major 500 kV transmission new project for the Bay Area and the re-scoping of two other projects in the San Jose area, will provide sufficient transmission capacity to meet long-term load growth needs.
Kifer – FMC 115 kV Line Reconductor | KIFER | FMC | PG&E | Reliability | 115 | 2.5 | 1400 A | 217 - 434 | Planned | 2032 | The set of 115 kV reinforcements proposed in this project, along with the major 500 kV transmission new project for the Bay Area and the re-scoping of two other projects in the San Jose area, will provide sufficient transmission capacity to meet long-term load growth needs.
Mountain View – Monta Vista 115 kV Line Reconductor | MOUNTAIN VIEW | MONTA VISTA | PG&E | Reliability | 115 | 4.78 | 3000 A | 217 - 434 | Planned | 2032 | The set of 115 kV reinforcements proposed in this project, along with the major 500 kV transmission new project for the Bay Area and the re-scoping of two other projects in the San Jose area, will provide sufficient transmission capacity to meet long-term load growth needs.
Whisman – Monta Vista 115 kV Line Reconductor | WHISMAN | MONTA VISTA | PG&E | Reliability | 115 | 5.97 | 3000 A | 217 - 434 | Planned | 2032 | The set of 115 kV reinforcements proposed in this project, along with the major 500 kV transmission new project for the Bay Area and the re-scoping of two other projects in the San Jose area, will provide sufficient transmission capacity to meet long-term load growth needs.
Metcalf - Piercy 115 kV Upgrade project | PIERCY | METCALF 2 | PG&E | Reliability | 115 | - | 3000 A | 124 - 248 | Planned | 2028 | The project originally proposed to reconductor the following 115 kV lines to 795 ACSS conductors or an equivalent: Piercy-Metcalf, Swift-Metcalf, and Newark-Dixon Landing. Project was approved in the 2003 Transmission Planning Process (TPP), was intended to alleviate these long-term overloads. However, due to significant increases in the load forecast, as cited in previous projects, and the additional load growth expectation in the San Jose area has motivated new transmission projects for the area and the re-scoping of existing ones.
Tesla - Newark 230 kV Line No. 2 Reconductoring | TESLA | NEWARK | PG&E | - | 230 | 4.28 | 3428 A | 29 - 58 | Planned | 2034 | To mitigate overloads identified as part of Interconnection Alternative E, the ISO recommends approval.
Tulucay-Napa #2 60 kV line Reconductoring project | TULUCAY | NAPA | PG&E | Reliability | 60 | - | - | 7.3 - 14.6 | Planned | 2027 | Expansion of previously approved project Tulucay-Napa #2 60 kV Line Capacity Increase to include line reconductoring.
TL695B Japanese Mesa Talega Tap Reconductor | MESA | TALEGA | SDG&E | Reliability | 69 | 10.24 | 60 MVA | - | Planned | 2028 | Eliminate NERC Category B violation to increase reliability by reconductoring TL 695 and TL 6971.
Rio Oso - W. Sacramento Reconductoring Project | RIO OSO | WEST SACRAMENTO | PG&E | - | 115 | 26 | - | 48.7-97.4 | Planned | 2030 | Reconductoring Rio Oso – W. Sacramento 115 kV line as original re-rate of this line as a part of Vaca Dixon reinforcement project approved in 2017-18 TPP is no longer viable due to aging infrastructure.
Reconductor Rio Oso–SPI Jct–Lincoln 115 kV line | RIO OSO | LINCOLN | PG&E | Reliability | 115 | 12 | - | - | Planned | 2028 | he new conductor will eliminate forecasted line overloads. PG&E proposes to replace wooden power poles with a combination of concrete, wood, and tubular steel poles (TSP) within the existing power line corridor.
Vaca-Plainfield 60 kV Line Reconductoring Project | VACAVILLE | PLAINFIELD | PG&E | - | 60 | 30 | 635 / 741 A | 34 - 68 | Planned | 2030 | Addressing the near-term overloads on the Vaca-Plainfield 60 kV line resulting from NERC Category P0 and P1 contingencies.
Wilson-Oro Loma 115kV Line Reconductoring | WILSON | ORO LOMA | PG&E | Reliability | 115 | 9 | 650 A | 11.3 - 22.7 | Planned | 2028 | The project will address thermal overloads in the Fresno area.
North Dublin - Vineyard 230 kV Reconductoring | NORTH DUBLIN | VINEYARD | PG&E | - | 230 | - | 1350 A | 116 - 232 | Planned | 2034 | To mitigate P1 overloads identified as part of Interconnection Alternative E, the ISO is recommending approval. It will take an estimated 24 months to complete.
Lugo - Victor-Kramer Upgrade (3/3) | VICTOR | KRAMER | SCE | - | 115/230 | - | - | 482/3 | Planned | 2033 | Rebuild/build Kramer–Victor 115 kV lines to 230 kV and Loop the old segment of Kramer–Victor 115 kV into Roadway